SECTION 33 0130 – Testing for Sanitary Sewage Gravity System

Maintain Section format, including the UH master spec designation and version date in bold in the center columns of the header and footer. Complete the header and footer with Project information

Edit and finalize this Section, where prompted by Editor’s notes, to suit Project specific requirements. Make selections for the Project at text identified in bold.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete hidden text after this Section has been edited for the Project.

1. GENERAL
	* + 1. RELATED DOCUMENTS
				1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
				2. The Contractor's attention is specifically directed, but not limited, to the following documents for additional requirements:

The current version of the *Uniform General Conditions for Construction Contracts*, State of Texas, available on the web site of the Texas Facilities Commission.

The University of Houston’s *Supplemental General Conditions and Special Conditions for Construction*.

* + - 1. SUMMARY
				1. This Section specifies the requirements for of all labor, materials, tools, and equipment to perform all operations in connection with leakage testing for completed manholes and gravity sewer pipe and deflection testing for flexible sewer pipe.
			2. APPLICABLE PUBLICATIONS
				1. The following publications of the latest issues listed below, but referred to thereafter by basic designation only, form a part of this Specification to the extent indicated by the references thereto.

American Society for Testing and Materials Standards (ASTM).

ASTM D 3034 - Standard Specification for Type PSM Polyethylene (Vinyl Chloride) (PVC) Sewer Pipe and Fittings.

ASTM F 794 - Specification for Poly (Vinyl Chloride) (PVC) Profile Gravity Sewer Pipe and Fittings Based on Controlled Inside Diameter.

ASTM F 1417 - Standard Test Method for Installation Acceptance of Plastic Gravity Sewer Lines Using Low Pressure Air.

ASTM C 1244 Standard Test Method for Concrete Sewer Manholes by the Negative Air Pressure (Vacuum) Test Prior to Backfill.

* + - 1. PROJECT CONDITIONS
				1. Gravity flow sanitary sewers must have straight alignment and uniform grade between manholes.
				2. Flexible pipe, including "semi-rigid" pipe, must show no more than 5 percent deflection. Test pipe no sooner than 30 days after backfilling of line segment but prior to final acceptance using standard mandrel to verify that installed pipe is within specified deflection tolerances.
				3. Work must meet Texas Commission on Environmental Quality (TCEQ) Testing Requirements Chapter-217-57.
				4. Interruption of Existing Storm Drainage Service: Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

Follow the University of Houston’s Plant Operations Planned and Emergency Utility Outage Guidelines. See “COORDINATION” Article in this Section.

* + - * 1. If work requires interference with any public sewer systems within or outside of Public Rights of Way or Easements, Contractor must obtain prior approval and coordinate with local municipality before commencing work.
			1. SUBMITTALS
				1. Test Plan: Before testing begins and in adequate time to obtain approval through submittal process, prepare and submit test plan for approval by Architect and Owner. Include testing procedures, methods, equipment, and tentative schedule. Obtain advance written approval from Architect and Owner for deviations from Drawings and Specifications.
				2. Test Reports: Submit test reports for each test on each segment of sanitary sewer.
			2. COORDINATION
				1. Complete the Outage Planning Form in the University of Houston’s Planned and Emergency Utility Outage Guidelines available in Section 00 6000 of these Specifications.
1. PRODUCTS
	* + 1. DEFLECTION MANDREL
				1. Mandrel Sizing. Rigid mandrel shall have outside diameter (O.D.) equal to 95 percent of inside diameter (I.D.) of pipe. Inside diameter of pipe, for purpose of determining outside diameter of mandrel, shall be average outside diameter minus two minimum wall thicknesses for O.D. controlled pipe and average inside diameter for I.D. controlled pipe. Dimensions shall be per appropriate standard. Statistical or other "tolerance packages" shall not be considered in mandrel sizing.
				2. Mandrel Design. Rigid mandrel shall be constructed of metal or rigid plastic material that can withstand 200 psi without being deformed. Mandrel shall have nine or more "runners" or "legs" as long as total number of legs is odd number. Barrel section of mandrel shall have length of at least 75 percent of inside diameter of pipe. Rigid mandrel shall not have adjustable or collapsible legs that would allow reduction in mandrel diameter during testing. Provide and use proving ring for modifying each size mandrel.
				3. Polyvinyl Chloride (PVC) pipe 4 inches in diameter shall be DR 18 and conform to AWWA C900. PVC pipe 6 to 10 inches in diameter shall be SDR 26 and conform to ASTM 3034. PVC pipe 12 to 15 inches diameter shall be SDR35 and conform to ASTM D3034. Polyvinyl chloride pipe 18 to 36 inches in diameter shall be SDR35 and conform to ASTM F679.
				4. Proving Ring. Furnish "proving ring" with each mandrel. Fabricate ring of 1/2-inch-thick, 3-inch-wide bar steel to diameter 0.02 inches larger than approved mandrel diameter.
				5. Mandrel Dimensions (5 percent allowance). Average inside diameter and minimum mandrel diameter are specified in Table 02533-5, Pipe vs. Mandrel Diameter, at end of this Section. Mandrels for higher strength, thicker wall pipe or other pipe not listed in table may be used when approved by Architect and Owner.
			2. EXFILTRATION TEST
				1. Water for Testing:

Water for testing will be furnished by the University; or

Obtain transient water meter from City for use when water for testing will be taken from City system. Conform to City requirements for water meter use.

* + - * 1. Test Equipment:

Pipe plugs.

Pipe risers where manhole cone is less than 2 feet above highest point in pipe or service lead.

* + - 1. INFILTRATION TEST
				1. Test Equipment:

Calibrated 90-degree V-notch weir.

Pipe plugs.

* + - 1. LOW PRESSURE AIR TEST
				1. Minimum Requirement for Equipment:

Control panel.

Low-pressure air supply connected to control panel.

Pneumatic plugs: Acceptable size for diameter of pipe to be tested; capable of withstanding internal test pressure without leaking or requiring external bracing.

Air hoses from control panel to:

Air supply.

Pneumatic plugs.

Sealed line for pressuring.

Sealed line for monitoring internal pressure.

* + - * 1. Testing Pneumatic Plugs: Place pneumatic plug in each end of length of pipe on ground. Pressurize plugs to 25 psig; then pressurize sealed pipe to 5 psig. Plugs are acceptable when they remain in place against test pressure without external aids.
			1. GROUND WATER DETERMINATION
				1. Equipment: Pipe probe or small diameter casing for ground water elevation determination.
1. EXECUTION
	* + 1. PREPARATION
				1. Provide labor, equipment, tools, test plugs, risers, air compressor, air hose, pressure meters, pipe probe, calibrated weirs, or any other device necessary for proper testing and inspection. Boring, Jacking or Tunneling Construction.
				2. Determine selection of test methods and pressures for gravity sanitary sewers based on ground water elevation. Determine ground water elevation.
			2. VISUAL INSPECTION OF GRAVITY SANITARY SEWERS
				1. Check pipe alignment visually by flashing light between structures. Verify if alignment is true and no pipes are misplaced. In case of misalignment or damaged pipe, remove and re-lay or replace pipe segment.
			3. MANDREL TESTING FOR GRAVITY SANITARY SEWERS
				1. Perform deflection testing on flexible and semi-rigid pipe to confirm pipe has no more than 5 percent deflection. Mandrel testing shall conform to ASTM D 3034. Perform testing no sooner than 30 days after backfilling of line segment, but prior to final acceptance testing of line segment.
				2. Pull approved mandrel by hand through sewer sections. Replace any section of sewer not passing mandrel test. Mandrel testing is not required for stubs.
				3. Retest repaired or replaced sewer sections.
			4. LEAKAGE TESTING FOR GRAVITY COLLECTION SYSTEM PIPES
				1. For a collection system pipe that will transport wastewater by gravity flow, test gravity sanitary sewer pipes for leakage by either exfiltration or infiltration methods, as appropriate, or with low pressure air testing.
				2. Compensating for Ground Water Pressure:

Where ground water exists, install pipe nipple at same time sewer line is placed. Use 1/2-inch capped pipe nipple approximately 10 inches long. Make installation through manhole wall on top of sewer line where line enters manhole.

Immediately before performing line acceptance test, remove cap, clear pipe nipple with air pressure, and connect clear plastic tube to nipple. Support tube vertically and allow water to rise in tube. After water stops rising, measure height in feet of water over invert of pipe. Divide this height by 2.3 feet/psi to determine ground water pressure to be used in line testing.

* + - * 1. Exfiltration Test:

Determine ground water elevation.

Plug sewer in downstream manhole.

Plug incoming pipes in upstream manhole.

Install riser pipe in outgoing pipe of upstream manhole when highest point in service lead (house service) is less than 2 feet below bottom of manhole cone.

Fill sewer pipe and manhole or pipe riser, when used, with water to point 2-1/2 feet above highest point in sewer pipe, house lead, or ground water table, whichever is highest.

Allow water to stabilize for one to two hours. Take water level reading to determine drop of water surface, in inches, over one-hour period, and calculate water loss (1 inch of water in 4 feet diameter manhole equals 8.22 gallons) or measure quantity of water required to keep water at same level. Loss shall not exceed that calculated from allowable leakage according to Table 1 at end of this Section.

* + - * 1. Infiltration test: Ground water elevation must be not less than 2.0 feet above highest point of sewer pipe or service lead (house service).

Determine ground water elevation.

Plug incoming pipes in upstream manhole.

Insert calibrated 90-degree V-notch weir in pipe on downstream manhole.

Allow water to rise and flow over weir until it stabilizes.

* + - * 1. Low Air Pressure Test: When using this test, conform to ASTM C 828, ASTM C 924, or ASTM F 1417, as applicable, with holding time not less than that listed in Table-2.

Low pressure air testing for sections of pipe shall be limited to lines less than 36-inch average inside diameter. Refer to Table-2 and Table-3.

Lines 36-inch average inside diameter and larger shall be tested at each joint. Minimum time allowable for pressure to drop from 3.5 pounds per square inch gauge to 2.5 pounds per square inch during joint test shall be 10 seconds, regardless of pipe size.

* + - * 1. Retest: Repair and retest any section of pipe that fails to meet requirements.
			1. TEST CRITERIA TABLES
				1. Exfiltration and Infiltration Water Tests: Refer to Table-1, Water Test Allowable Leakage, at end of this Section.
				2. Low Pressure Air Test:

Times in Table 02533-2, Time Allowed for Pressure Loss from 3.5 psig to 2.5 psig, at end of this Section, are based on equation from Texas Commission on Environmental Quality (TCEQ) Design Criteria 217.57.

|  |  |  |
| --- | --- | --- |
|  |  | T=0.0850(D)(K)/(Q) |
| Where: | T = | Time for pressure to drop 1.0 pounds per square inch gauge in seconds |
|  | K = | 0.000419 DL, but not less than 1.0 |
|  | D = | Average inside diameter in inches |
|  | L = | Length of line of same pipe size in feet |
|  | Q = | Rate of loss, 0.0015 ft3/min./sq. ft. internal surface |

Since K value of less than 1.0 shall not be used, there are minimum testing times for each pipe diameter as given in Table 02533-3, Minimum Testing Times for Low Pressure Air Test.

Notes:

When two sizes of pipe are involved, compute time by ratio of lengths involved.

Lines with 27-inch average inside diameter and larger may be air tested at each joint.

Lines with average inside diameter greater than 36 inches must be air tested for leakage at each joint.

If joint test is used, perform visual inspection of joint immediately after testing.

For joint test, pipe is to be pressurized to 3.5 psi greater than pressure exerted by groundwater above pipe. Once pressure has stabilized, minimum times allowable for pressure to drop from 3.5 pounds per square inch gauge to 2.5 pounds per square inch gauge shall be 10 seconds.

* + - 1. LEAKAGE TESTING FOR MANHOLES
				1. After completion of manhole construction, wall sealing, or rehabilitation, but prior to backfilling, test manholes for water tightness using hydrostatic or vacuum testing procedures.
				2. Plug influent and effluent lines, including service lines, with suitably sized pneumatic or mechanical plugs. Ensure plugs are properly rated for pressures required for test; follow manufacturer's safety and installation recommendations. Place plugs minimum of 6-inches outside of manhole walls. Brace inverts to prevent lines from being dislodged when lines entering manhole have not been backfilled.
				3. Perform vacuum testing as follows:

Install vacuum tester head assembly at top access point of manhole and adjust for proper seal on straight top section of manhole structure. Following manufacturer's instructions and safety precautions, inflate sealing element to recommended maximum inflation pressure; do not over-inflate.

Evacuate manhole with vacuum pump to 10 inches mercury (Hg), disconnect pump, and monitor vacuum for time period specified in Table-4, Vacuum Test Time Table.

A manhole passes the test if after 2.0 minutes and with all valves closed, the vacuum is at least 9.0 inches of mercury (Hg).

* + - * 1. Perform hydrostatic exfiltration testing as follows:

Seal wastewater lines coming into manhole with internal pipe plug. Then fill manhole with water and maintain it full for at least one hour.

The maximum leakage for hydrostatic testing shall be 0.025 gallons per foot diameter per foot of manhole depth per hour.

If water loss exceeds amount tabulated above, locate leaks, complete repairs necessary to seal manhole, and repeat test procedure until satisfactory results are obtained.

TABLE-1 - WATER TEST ALLOWABLE LEAKAGE

|  |  |  |
| --- | --- | --- |
| DIAMETER OF RISER OR STACK IN INCHES | VOLUME PER INCH OF DEPTH | ALLOWANCE LEAKAGE\* |
| INCH | GALLONS | PIPE SIZE IN INCHES | GALLONS/MINUTE PER 100 FT. |
| 122.534568 | 0.78543.14164.90877.068612.566419.635028.274350.2655 | 0.00340.1360.2120.03060.05440.08500.12240.2176 | 6810121518212427303642 | 0.00080.00110.00170.00160.00200.00240.00280.00320.00360.00390.00470.0055 |
| For other diameters, multiply square of diameters by value for 1-inch diameter. | Equivalent to 10 gallons per inch of inside diameter per mile per 24 hours |

\*Allowable leakage rate must not exceed 10 gallons per inch of inside diameter per mile per 24 hours, when sewer is identified as located within 25-year flood plain.

TABLE-2 – ACCEPTANCE TESTING FOR SANITARY SEWERS

|  |
| --- |
| TIME ALLOWED FOR PRESSURE LOSS FROM 3.5 PSIG TO 2.5 PSIG |
| PIPE DIAM. (IN) | MIN TIME (MIN:SEC) | LENGTH FOR MIN. TIME(FT) | Time for Longer Length (sec) | Specification Time for Length (L) Shown (min:sec) |
| 100 ft | 150 ft | 200 ft | 250 ft | 300 ft | 350 ft | 400 ft | 450 ft | 500 ft | 550 ft | 600 ft |
| 68101215182124273033 | 5:407:339:2711:2014:1017:0019:5022:4025:3028:2031:10 | 39829823919915913311499888072 | 0.85481.51962.37433.41905.34237.692810.470813.676217.308921.639025.8565 | 5:407:339:2711:2014:1017:0019:5022:4828:5135:3743:06 | 5:407:339:2711:2014:1019:1426:1134:1143:1653:2564:38 | 5:407:339:2711:2017:4825:3934:5445:3557:4271:1486:11 | 5:407:339:5414:1522:1632:0343:3856:5972:0789:02107:44 | 5:407:3611:5217:0626:4338:2852:2168:2386:33106:51129:17 | 5:408:5213:5119:5731:1044:5261:0579:47100:58124:39150:50 | 5:4210:0815:5022:4835:3751:1769:4891:10115:24142:28172:23 | 6:2511:2417:4825:3940:0457:4278:32102:34129:49160:16193:55 | 7:0712:4019:4728:3044:3164:0687:15113:58144:14178:05215:28 | 7:5013:5621:4631:2048:5870:3198:59125:22128:40195:53237:01 | 8:3315:1223:4534:1153:2576:56104:42136:46173:05213:41258:34 |

TABLE-3 – MINIMUM TESTING TIMES FOR LOW PRESSURE AIR TEST

|  |  |  |  |
| --- | --- | --- | --- |
| PIPE DIAMETER(INCHES) | MINIMUM TIME(SECONDS) | LENGTH FOR MINIMUM TIME(FEET) | TIME FOR LONGER LENGTH(SECONDS/FT) |
| 68101215182124273033 | 340454567680850102011901360153017001870 | 398298239199159133114100888072 | 0.8551.5202.3743.4195.3427.69310.47113.67617.30921.36925.856 |

TABLE-4 – VACUUM TEST TIME TABLE

|  |  |
| --- | --- |
| DEPTH IN FEET | TIME IN SECONDS BY PIPE DIAMETER |
|  | 48inch | 60inch | 72inch |
| 4812162024\* | 1020304050605.0 | 1326395265786.5 | 1632486480968.0 |
| \*Add T times for each additional 2-foot depth.(The values listed above have been extrapolated from ASTM C 1244) |

TABLE-5 PIPE VS. MANDREL DIAMETER

|  |  |  |  |
| --- | --- | --- | --- |
|  Material and Wall Construction | Nominal Size (Inches) | Average I.D. (Inches) | Minimum Mandrel Diameter (Inches) |
| PVC -Solid (SDR 26)5.476 | 6810 | 67.7159.646 | 5.7647.3299.162 |
| PVC-Solid (SDR 35)11.150 | 121518212427 | 1214.37417.62920.78323.38126.351 | 11.73713.65516.74819.74422.12025.033 |

* + - 1. FIELD QUALITY ASSURANCE
				1. Repair, correct, and retest manholes or sections of pipe that fail to meet specified requirements when tested.
				2. Provide testing reports and video tape of television inspection as directed by Architect and Owner.
				3. Upon completion of tape reviews by Architect and Owner, Contractor will be notified regarding final acceptance of sewer segment.
				4. Perform testing as work progresses. Schedule testing so that no more than 1000 linear feet of installed sewer remains untested at one time.
				5. Coordinate testing schedules with Owner. Perform testing under observation of Architect and Owner.

END OF SECTION 33 0130