SECTION 26 5619 - LED EXTERIOR LIGHTING

Maintain Section format, including the UH master spec designation and version date in bold in the center columns of the header and footer.  Complete the header and footer with Project information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Delete hidden text after this Section has been edited for the Project.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

        - The Contractor's attention is specifically directed, but not limited, to the following documents for additional requirements:

          - The current version of the Uniform General Conditions for Construction Contracts, State of Texas, available on the web site of the Texas Facilities Commission.

          - The University of Houston’s Supplemental General Conditions and Special Conditions for Construction.

      - SUMMARY

        - Section Includes:

          - Exterior solid-state luminaires that are designed for and exclusively use LED lamp technology.

          - Luminaire supports.

          - Luminaire mounted photoelectric relays.

        - Work included:

          - Furnish and install luminaire fixtures of the types indicated by letter at each location shown on the Drawings.

          - Provide materials, accessories, and any other equipment necessary for the complete and proper installation of luminaire fixtures included in this Contract.

          - Conformance:  Luminaire fixture shall be manufactured in strict accordance with the Contract Drawings and Specifications.

          - Specifications and scale Drawings are intended to convey the salient features, function and character of the fixtures only, and do not undertake to illustrate or set forth every item or detail necessary for the work.

          - Minor details, not usually indicated on the Drawings nor specified, but that are necessary for the proper execution and completion of the fixtures, shall be included, the same as if they were herein specified or indicated on the Drawings.

          - Omissions:  The Owner shall not be held responsible for the omission or absence of any detail, construction feature, etc. which may be required in the production of the fixtures.  The responsibility of accurately fabricating the fixtures to the fulfillment of this specification rests with Contractor.

      - DEFINITIONS

        - CCT: Correlated color temperature.

        - CRI: Color rendering index.

        - Fixture: See "Luminaire."

        - IP: International Protection or Ingress Protection Rating.

        - Lumen: Measured output of lamp and luminaire, or both.

        - Luminaire: Complete lighting unit, including lamp, reflector, and housing.

      - ACTION SUBMITTALS

        - Product Data: For each type of luminaire.

          - Arrange in order of luminaire designation.

          - Include data on features, accessories, and finishes.

          - Include physical description and dimensions of luminaire.

          - Lamps, include life, output (lumens, CCT, and CRI), and energy-efficiency data.

          - Photometric data and adjustment factors based on laboratory tests, complying with IES Lighting Measurements Testing and Calculation Guides, of each luminaire type. The adjustment factors shall be for lamps and accessories identical to those indicated for the luminaire as applied in this Project IES LM-79 and IES LM-80.

            - Manufacturer's Certified Data: Photometric data certified by manufacturer's laboratory with a current accreditation under the NVLAP for Energy Efficient Lighting Products.

          - Wiring diagrams for power, control, and signal wiring.

          - Photoelectric relays.

          - Means of attaching luminaires to supports and indication that the attachment is suitable for components involved.

        - Shop Drawings: For nonstandard or custom luminaires.

          - Include plans, elevations, sections, and mounting and attachment details.

          - Include details of luminaire assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

        - Samples: For each luminaire and for each color and texture indicated with factory-applied finish.

        - Product Schedule: For luminaires and lamps. Use same designations indicated on Drawings.

      - INFORMATIONAL SUBMITTALS

        - Coordination Drawings: Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

          - Luminaires.

          - Structural members to which equipment and luminaires will be attached.

          - Underground utilities and structures.

          - Existing underground utilities and structures.

          - Above-grade utilities and structures.

          - Existing above-grade utilities and structures.

          - Building features.

          - Vertical and horizontal information.

        - Qualification Data: For testing laboratory providing photometric data for luminaires.

        - Product Certificates: For each type of the following:

          - Luminaire.

          - Photoelectric relay.

        - Product Test Reports: For each luminaire, for tests performed by manufacturer and witnessed by a qualified testing agency.

        - Source quality-control reports.

        - Sample warranty.

      - QUALITY ASSURANCE

        - Luminaire Photometric Data Testing Laboratory Qualifications, Luminaire manufacturers' laboratory that is accredited under the NVLAP for Energy Efficient Lighting Products.

        - Provide luminaires from a single manufacturer for each luminaire type.

        - Each luminaire type shall be binned within a three-step MacAdam Ellipse to ensure color consistency among luminaires.

        - Installer Qualifications: An authorized representative who is trained and approved by manufacturer.

      - DELIVERY, STORAGE, AND HANDLING

        - Protect finishes of exposed surfaces by applying a strippable, temporary protective covering prior to shipping.

      - FIELD CONDITIONS

        - Verify existing and proposed utility structures prior to the start of work associated with luminaire installation.

        - Mark locations of exterior luminaires for approval by Architect prior to the start of luminaire installation.

- PRODUCTS

      - MANUFACTURER

        - Products: Subject to compliance with requirements, provide product indicated and scheduled on Drawings and related contract documents.  Only listed fixtures can be used.  Substitutions are not acceptable.

        - First luminaire fixtures listed for each type in the luminaire fixture schedule are the basis of design (BOD) and have been used in calculating lighting levels and energy code compliance.  Perform studies and verify compliance with requirements upon selection of a different fixture in the schedule from the BOD.

      - PERFORMANCE REQUIREMENTS

        - Ambient Temperature:  -20o F to 104o F.

          - Relative Humidity:  Zero to 100 percent.

        - Altitude:  Minimum 1000 feet.

      - LUMINAIRE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - NRTL Compliance: Luminaires shall be listed and labeled for indicated class and division of hazard by an NRTL.

        - UL Compliance: Comply with UL 1598 and listed for wet location.

        - L70 lamp life of 50,000 hours.

        - Lamps dimmable from 100 percent to 0 percent of maximum light output.

        - Internal driver.

        - Nominal Operating Voltage:  Multi-volt.

        - In-line Fusing:  Separate in-line fuse for each luminaire.

        - Lamp Rating: Lamp marked for outdoor use.

        - Color Temperature: 4000K.

        - CRI: 90 or better.

        - Source Limitations: Obtain luminaires from single source from a single manufacturer.

        - Source Limitations: For luminaires, obtain each color, grade, finish, type, and variety of luminaire from single source with resources to provide products of consistent quality in appearance and physical properties.

      - LUMINAIRE-MOUNTED PHOTOELECTRIC RELAYS

        - Comply with UL 773 or UL 773A.

        - Contact Relays: Factory mounted, single throw, designed to fail in the on position, and factory set to turn light unit on at 1.5 to 3 fc and off at 4.5 to 10 fc with 15-second minimum time delay. Relay shall have directional lens in front of photocell to prevent artificial light sources from causing false turnoff.

          - Relay with locking-type receptacle shall comply with ANSI C136.10.

          - Adjustable window slide for adjusting on-off set points.

      - MATERIALS

        - Metal Parts: Free of burrs and sharp corners and edges.

        - Sheet Metal Components:  Epoxy-coated steel. Form and support to prevent warping and sagging.

        - Doors, Frames, and Other Internal Access: Smooth operating, free of light leakage under operating conditions, and designed to permit re-lamping without use of tools. Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during re-lamping and when secured in operating position. Doors shall be removable for cleaning or replacing lenses.

        - Diffusers and Globes:

          - Acrylic Diffusers: 100 percent virgin acrylic plastic, with high resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

          - Glass: Annealed crystal glass unless otherwise indicated.

          - Lens Thickness: At least 0.125 inch minimum unless otherwise indicated.

        - Lens and Refractor Gaskets: Use heat- and aging-resistant resilient gaskets to seal and cushion lenses and refractors in luminaire doors.

        - Reflecting surfaces shall have minimum reflectance as follows unless otherwise indicated:

          - White Surfaces: 85 percent.

          - Specular Surfaces: 83 percent.

          - Diffusing Specular Surfaces: 75 percent.

        - Housings:

          - Rigidly formed, weather- and light-tight enclosure that will not warp, sag, or deform in use.

          - Provide filter/breather for enclosed luminaires.

        - Factory-Applied Labels: Comply with UL 1598. Include recommended lamps. Labels shall be located where they will be readily visible to service personnel, but not seen from normal viewing angles when lamps are in place.

          - Label shall include the following lamp characteristics:

            - "USE ONLY" and include specific lamp type.

            - Lamp diameter, shape, size, wattage and coating.

            - CCT and CRI for all luminaires.

      - FINISHES

        - Variations in Finishes: Noticeable variations in same piece are unacceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

        - Luminaire Finish: Manufacturer's standard paint applied to factory-assembled and -tested luminaire before shipping. Where indicated, match finish process and color of pole or support materials.

        - Factory-Applied Finish for Steel Luminaires: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

          - Surface Preparation: Clean surfaces to comply with SSPC-SP 1, to remove dirt, oil, grease, and other contaminants that could impair paint bond. Grind welds and polish surfaces to a smooth, even finish. Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1 or SSPC-SP 8.

          - Exterior Surfaces: Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

            - Color: Black.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for luminaire electrical conduit to verify actual locations of conduit connections before luminaire installation.

        - Examine walls, roofs, and canopy ceilings and overhang ceilings for suitable conditions where luminaires will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - TEMPORARY LIGHTING

        - If approved by the Architect, use selected permanent luminaires for temporary lighting. When construction is substantially complete, clean luminaires used for temporary lighting and install new lamps.

      - GENERAL INSTALLATION REQUIREMENTS

        - Comply with NECA 1.

        - Install lamps in each luminaire.

        - Fasten luminaire to structural support.

        - Supports:

          - Sized and rated for luminaire weight.

          - Able to maintain luminaire position after cleaning and re-lamping.

          - Support luminaires without causing deflection of finished surface.

          - Luminaire-mounting devices shall be capable of supporting a horizontal force of 100 percent of luminaire weight and a vertical force of 400 percent of luminaire weight.

        - Wall-Mounted Luminaire Support:

          - Attached to a minimum 1/8-inch backing plate attached to wall structural members.

        - Wiring Method: Install cables in raceways. Conceal raceways and cables.

        - Install luminaires level, plumb, and square with finished grade unless otherwise indicated. Install luminaires at height and aiming angle as indicated on Drawings.

        - Coordinate layout and installation of luminaires with other construction.

        - Adjust luminaires that require field adjustment or aiming. Include adjustment of photoelectric device to prevent false operation of relay by artificial light sources, favoring a north orientation.

        - Comply with requirements in Division26 Sections "Low-Voltage Electrical Power Conductors and Cables" and "Raceways and Boxes for Electrical Systems" for wiring connections and wiring methods.

      - PEDESTRIAN POLE LUMINAIRE INSTALLATION

        - Align units for optimum directional alignment of light distribution.

          - Install on concrete base with top 4 inches above finished grade or with top flush with surrounding plaza surface at luminaire location. Cast conduit into base and finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Division 03 Section "Cast-in-Place Concrete."

      - INSTALLATION OF INDIVIDUAL GROUND-MOUNTED LUMINAIRES

        - Aim as indicated on Drawings.

        - Install on concrete base with top 4 inches above finished grade or flush with paving surface at luminaire location. Cast conduit into base, and finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Division 03 Section "Cast-in-Place Concrete."

      - CORROSION PREVENTION

        - Aluminum: Do not use in contact with earth or concrete. When in direct contact with a dissimilar metal, protect aluminum by insulating fittings or treatment.

        - Steel Conduits: Comply with Division 26 Section "Electrical Raceways." In concrete foundations, wrap conduit with 0.010-inch thick, pipe-wrapping plastic tape applied with a 50 percent overlap.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."

      - FIELD QUALITY CONTROL

        - Inspect each installed luminaire for damage. Replace damaged luminaires and components.

        - Perform the following tests and inspections with the assistance of a factory-authorized service representative:

          - Operational Test: After installing luminaires, switches, and accessories, and after electrical circuitry has been energized, test units to confirm proper operation.

          - Verify operation of photoelectric controls.

        - Illumination Tests:

          - Measure light intensities at night. Use photometers with calibration referenced to NIST standards. Comply with the following IES testing guide(s):

            - IES LM-64.

          - Operational Test: After installing luminaires, switches, and accessories, and after electrical circuitry has been energized, test units to confirm proper operation.

        - Luminaire will be considered defective if it does not pass tests and inspections.

        - Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results. If adjustments are made to lighting system, retest to demonstrate compliance with standards.

        - Prepare and submit a final foot-candle record analysis of the exterior lighting system.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain luminaires and photocell relays.

      - ADJUSTING

        - Occupancy Adjustments: When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting the direction of aim of luminaires to suit occupied conditions. Make up to two visits to Project during other-than-normal hours for this purpose. Some of this work may be required during hours of darkness.

          - During adjustment visits, inspect all luminaires. Replace lamps or luminaires that are defective.

          - Parts and supplies shall be manufacturer's authorized replacement parts and supplies.

          - Adjust the aim of luminaires in the presence of the Architect.

END OF SECTION 26 5619