Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 072726 - FLUID-APPLIED MEMBRANE AIR BARRIERS

- GENERAL

      - SUMMARY

        - Section includes fluid-applied, vapor-permeable membrane air barriers.

      - PREINSTALLATION MEETINGS

        - Preinstallation Conference:  Conduct conference at Project site.

      - ACTION SUBMITTALS

        - Product Data:  For each type of product.

        - Shop Drawings:  For air-barrier assemblies.

          - Include details for through-wall flashings, substrate joints and cracks, counterflashing strips, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction.

      - INFORMATIONAL SUBMITTALS

        - Product certificates.

        - Product test reports.

      - QUALITY ASSURANCE

        - Installer Qualifications:  An entity that employs installers and supervisors who are trained and approved by manufacturer.

        - Mockups:  Build mockups to set quality standards for materials and execution.

          - Build integrated mockups of exterior wall assembly as shown on Drawings, incorporating backup wall construction, external cladding, window, storefront, door frame and sill, insulation, ties and other penetrations, and flashing to demonstrate surface preparation, crack and joint treatment, application of air barriers, and sealing of gaps, terminations, and penetrations of air-barrier assembly.

            - Coordinate construction of mockups to permit inspection by Owner's testing agency of air barrier before external insulation and cladding are installed.

            - Include junction with roofing membrane and foundation wall intersection.

      - WARRANTY

        - Provide manufactures standard 10-year material warranty.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

Retain one of first two options in "General" Paragraph below depending on whether a vapor-retarding or -permeable air barrier is required.  Consider retaining third option if air barrier serves as a primary or secondary drainage plane.

        - General:  Air barrier shall be capable of performing as a continuous vapor- permeable air barrier and as a liquid-water drainage plane flashed to discharge to the exterior incidental condensation or water penetration.  Air-barrier assemblies shall be capable of accommodating substrate movement and of sealing substrate expansion and control joints, construction material changes, penetrations, and transitions at perimeter conditions without deterioration and air leakage exceeding specified limits.

      - VAPOR-PERMEABLE MEMBRANE AIR BARRIER

Generally retain this article for a membrane air barrier located on the warm side of primary wall insulation.  These membranes are materials with an installed dry film thickness of about 40 mils (1.0 mm) and thicker.VAPOR-PERMEABLE MEMBRANE AIR-BARRIER

Generally retain this article for a membrane air barrier located on the cold side of primary wall insulation.  A separate vapor retarder may also be required at a different location within the wall.  These membranes are materials with an installed dry film thickness of about 40 mils (1.0 mm) and thicker.

        - Fluid-Applied, Vapor-Permeable Membrane Air Barrier:  Synthetic polymer membrane.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Synthetic Polymer Membrane:

              - Henry Company; Air-Bloc 31.

              - Grace, W. R., & Co. - Conn.; Perm-A-Barrier VP.

              - Tremco Incorporated, an RPM company; ExoAir 230.

          - Physical and Performance Properties:

Air-permeance value in "Air Permeance" Subparagraph below is based on ABAA requirements and energy-conservation requirements of the Massachusetts State Building Code, 780 CMR, Ch. 13.

            - Air Permeance:  Maximum 0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft. (0.02 L/s x sq. m of surface area at 75-Pa) pressure difference; ASTM E 2178.

Vapor-permeance values in "Vapor Permeance" Subparagraph below are based on some listed products.

            - Vapor Permeance:  Minimum 5.5 perms (320 ng/Pa x s x sq. m); ASTM E 96/E 96M.

            - Ultimate Elongation:  Minimum 400 percent; ASTM D 412, Die C.

      - ACCESSORY MATERIALS

        - General:  Accessory materials recommended by air-barrier manufacturer to produce a complete air-barrier assembly and compatible with primary air-barrier material.

Foam sealant in "Sprayed Polyurethane Foam Sealant" Paragraph below is used to fill gaps at penetrations and openings.

        - Sealant:  a moisture cure, medium modulus polymer modified sealing compound compatible with sheet air barrier, roofing and waterproofing membranes and substrate.

        - Termination Mastic:  Air-barrier manufacturer's standard cold fluid-applied elastomeric liquid; trowel grade.

        - Primers: Water based, low VOC as provided by the manufacturer.

        - Transition Flashing: 40 mil SBS modified bitumen self-adhering membrane with a cross-laminated polyethylene film for window and door sill flashing, door openings, inside and outside corners and other transitions as provided by the manufacturer.

- EXECUTION

      - SURFACE PREPARATION

        - Mask off adjoining surfaces not covered by air barrier to prevent spillage and overspray affecting other construction.

        - Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids in concrete with substrate-patching membrane.

        - Remove excess mortar from masonry ties, shelf angles, and other obstructions.

        - At changes in substrate plane, apply sealant or termination mastic beads at sharp corners and edges to form a smooth transition from one plane to another.

      - INSTALLATION

Revise this article to coordinate with drawing details.  Place sheet or liquid-seal materials over a firm backing to provide structural support for achieving an effective and permanent air barrier.

        - General:  Install fluid-applied membrane air-barrier using spray equipment and accessory materials according to air-barrier manufacturer's written instructions to form a seal with adjacent construction and maintain a continuous air barrier.

          - Coordinate the installation of air barrier with installation of roofing membrane and base flashing to ensure continuity of air barrier with roofing membrane.

          - Install air-barrier assembly on roofing membrane or base flashing so that a minimum of 3 inches (75 mm) of coverage is achieved over each substrate.

          - Sequence Work so that detailing of self-adhered membrane flashing is completed prior to the installation of the fluid applied membrane.

        - Apply primer to substrates at required rate and allow it to dry.  Limit priming to areas that will be covered by fluid air-barrier material on same day.  Reprime areas exposed for more than 24 hours.

Retain subparagraph below if using glass-fiber-surfaced gypsum sheathing.

          - Prime glass-fiber-surfaced gypsum sheathing with number of prime coats needed to achieve required bond, with adequate drying time between coats.

        - Joint Treatments:

          - Seal joints ¼ inch and less between panels of exterior grade gypsum, DensGlass Gold, plywood, OSB or cementitious panels with joint treatment sealant.

          - Seal gaps and voids or irregular joints greater than ¼ inch between panels of exterior grade gypsum, DensGlass Gold, plywood, OSB or cementitious panels with a strip of self-adhering air/vapor barrier transition membrane lapped a minimum of 1 1/2 inches on both sides of the joint.

          - Alternately, joints not exceeding 1/8 inch can be sealed with yellow open weave glass fabric.

        - Connect and seal exterior wall air-barrier material continuously to roofing-membrane air barrier, concrete below-grade structures, floor-to-floor construction, exterior glazing and window systems, glazed curtain-wall systems, storefront systems, exterior louvers, exterior door framing, and other construction used in exterior wall openings, using accessory materials.

        - At end of each working day, seal top edge of air barrier to substrate with termination mastic.

        - Wall Openings:  Prime concealed, perimeter frame surfaces of windows, curtain walls, storefronts, and doors.  Apply transitions and flashing so that a minimum of 3 inches (75 mm) of coverage is achieved over each substrate.  Maintain 3 inches (75 mm) of full contact over firm bearing to perimeter frames with not less than 1 inch (25 mm) of full contact.

        - Seal air-barrier assembly around masonry reinforcing or ties and penetrations with termination mastic.

        - Seal top of through-wall flashings to air barrier.

        - Seal exposed edges of strips at seams, cuts, penetrations, and terminations not concealed by metal counterflashings or ending in reglets with termination mastic.

        - Repair punctures, voids, and deficient lapped seams.  Slit and flatten fishmouths and blisters.  Extend patches 6 inches (150 mm) beyond repaired areas.

        - Fluid-Applied Membrane Material:  Apply a continuous unbroken air-barrier membrane to substrates according to the following thickness.  Apply air-barrier membrane in full contact around protrusions such as masonry ties.

Retain "Vapor-Retarding Membrane Air Barrier" or "Vapor-Permeable Membrane Air Barrier" Subparagraph below.  If specifying a thickness dimension, verify thickness or thickness range recommended by manufacturers; recommended thickness varies with product and may vary with substrate.

          - Vapor-Permeable Membrane Air Barrier:  Total 45-mil (1.1-mm) dry film thickness, applied in  one or more equal coats with spray equipment recommended by the manufacturer.

        - Do not cover air barrier until it has been tested and inspected by Owner's testing agency.

        - Correct deficiencies in or remove air barrier that does not comply with requirements; repair substrates and reapply air-barrier components.

      - FIELD QUALITY CONTROL

Coordinate test and inspection requirements in this article with Owner's testing agency.

        - Testing Agency:  Owner will engage a qualified testing agency to perform tests and inspections.

        - Inspections:  Air-barrier materials, accessories, and installation are subject to inspection for compliance with requirements.

        - Tests:  As determined by Owner's testing agency from among the following tests:

Retain "Qualitative Air-Leakage Testing" Subparagraph below if testing to locate air-leakage sites is required and if quantitative air-leakage testing is required.

Retain "Quantitative Air-Leakage Testing" Subparagraph below if testing to quantify air-leakage rate is required.

          - Quantitative Air-Leakage Testing:  Air-barrier assemblies will be tested for air leakage according to ASTM E 783.

          - Adhesion Testing:  Air-barrier assemblies will be tested for minimum air-barrier adhesion of 30 lbf/sq. in. (207 kPa) according to ASTM D 4541 for each 600 sq. ft. (56 sq. m) of installed air barrier or part thereof.

        - Air barriers will be considered defective if they do not pass tests and inspections.

          - Apply additional air-barrier material, according to manufacturer's written instructions, where inspection results indicate insufficient thickness.

          - Remove and replace deficient air-barrier components for retesting as specified above.

        - Repair damage to air barriers caused by testing; follow manufacturer's written instructions.

        - Protect air-barrier system from damage during application and remainder of construction period, according to manufacturer's written instructions.

          - Protect air barrier from exposure to UV light and harmful weather exposure as required by manufacturer.  If exposed to these conditions for more than 60 days, remove and replace air barrier or install additional, full-thickness, air-barrier application after repairing and preparing the overexposed membrane according to air-barrier manufacturer's written instructions.

          - Protect air barrier from contact with incompatible materials and sealants not approved by air-barrier manufacturer.

        - Remove masking materials after installation.

END OF SECTION 072726